## Sheet1
Wiring details for Vineyard monitoring station
Base (mandatory) devices					Auxilary (optional) sensors
Device	Channel	Color	CR3000		Device	Channel	Color	CR3000
control box for / sonic, IRGA / (EC100)	SDM data	green	SDM-C1		Univ. of Idaho / light sensors / (Decagon)	digital out (SDI)	red	C5
	SDM clock	white	SDM-C2			excitation	white	12V
	SDM enable	red	SDM-C3			ground	bare	G
	SDM reference	black	G		N2O/CO analyzer / (Los Gatos)	N2O signal	-	DIFF 8H
	SDM shield	clear	G			N2O reference	-	DIFF 8L
	power in	red	Terminal strip			CO signal	-	DIFF 9H
	power ground	black				CO reference	-	DIFF 9L
Wind set / (034B)	WD signal	green	SE 1			H2O signal	-	DIFF 10H
	WD excitation	blue	VX 1			H2O reference	-	DIFF 10L
	WD reference	white	earth		CO2/CH4 analyzer / (Picarro)	CO2 signal	-	DIFF 11H
	WS signal	red	P1			CO2 reference	-	DIFF 11L
	WS reference	black	earth			CH4 signal	-	DIFF 12H
	shield	clear	earth			CH4 reference	-	DIFF 12L
Temp/RH probe / (HMP-155A)	temp signal	yellow	DIFF 2H			H2O signal	-	DIFF 13H
	RH signal	blue	DIFF 3H			H2O reference	-	DIFF 13L
	signal reference	white	DIFF 2L + 3L		Heat flux plate #1 / (HFP01SC) / S/N: 2373	sensor signal	white	DIFF 6H
	power in	red	12V			sensor reference	green	DIFF 6L
	power ground	black	G			shield	clear	earth
	shield	clear	earth			heater signal	yellow	SE 27
Rain gage / (TE 525)	rain signal	black	P2			heater reference	purple	earth
	signal reference	white	earth			shield	clear	earth
	shield	clear	earth			power in	red	SW12-1
Net radiometer / (NR-Lite2)	net rad signal	red	DIFF 4H			power ground	black	G
	signal reference	blue	DIFF 4L + earth		Heat flux plate #2 / (HFP01SC) / S/N: 2384	sensor signal	white	DIFF 7H
	shield	black	earth			sensor reference	green	DIFF 7L
PAR sensor / (LI-190SB)	PAR signal	red	DIFF 5H			shield	clear	earth
	signal reference	black	DIFF 5L + earth			heater signal	yellow	SE 28
	shield	clear	earth			heater reference	purple	earth
soil moisture probes / (5TM)	digital out (SDI)	red	C5			shield	clear	earth
	excitation	white	12V			power in	red	SW12-1
	ground	bare	G			power ground	black	G
GPS / (GPS16X-HVS)	msg trasmit (TX)	white	COM 4 Rx
	PPS	gray	COM 4 Tx
	receive data (RX)	blue	G
	shield	clear	G	Solar controller connections		Terminal strip connections
	power in	red	12V	Solar (+)	Solar panels (+)	(+)	CR3000	power 12V/red
	power ground	black	G	Solar (-)	Solar panels (-)		EC100	power 12V/red
	power switch	yellow	G	Battery (+)	Batteries (+)		RavenXT	power 12V/red
Broadband modem / (RavenXT+SC105)	power switch	white	Terminal strip		Terminal strip (+)	(-)	CR3000	power G/black
	power in	red		Battery (-)	Batteries (+)		EC100	power G/black
	power ground	black			Terminal strip (-)		RavenXT	power G/black